| Purpose |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| This form is to certify the electrical safety of newly designed and/or modified electrical equipment by, or for the ANU. Note: Ensure the design and/or manufacture/modification of any electrical equipment complies with the requirements of s22 of the Work Health and Safety Act 2011 (Cth) and applicable regulations in Part 4.7 of the Work Health and Safety Regulations 2011 (Cth). Contact whs@anu.edu.au for advice or assistance. |  |  |  |  |  |  |  |
| Instructions |  |  |  |  |  |  |  |
| This form is to be completed by an authorised person prior to the introduction of an item to service. Once completed forward a copy to whs@anu.edu.au within two (2) weeks of commencement of service. |  |  |  |  |  |  |  |
| Equipment Details |  |  |  |  |  |  |  |
| Equipment Title |  |  |  |  |  |  |  |
| Equipment Model |  |  |  |  | Serial No/s |  |  |
| Designer |  |  |  |  | Date |  |  |
| School and Dept. |  |  |  |  |  |  |  |
| Certification No |  |  | C |  |  |  |  |
| Description |  |  |  |  |  |  |  |
| Checklist (tick in the corresponding box as appropriate) |  |  |  |  |  |  |  |
| The list below is to be used as a prompt only. Other faults may need to be additionally identified. Add extra pages if necessary. |  |  |  |  |  |  |  |
| 1. Equipment External |  |  |  |  |  |  |  |
| ☐ | - Power attachment – (secure, conforms to Aust. Standards, Power consumption labelled appropriately, etc.). |  |  |  |  |  |  |
| ☐ | - Earthing (all exposed metal appropriately connected, earth attachment labelled). |  |  |  |  |  |  |
| ☐ | - Guards / protection (guards securely in place, protection devices e.g. thermal cut-outs operational). |  |  |  |  |  |  |
| ☐ | - Controls (suitable for task, clearly labelled, Power Switch “OFF” position labelled, etc.). |  |  |  |  |  |  |
| ☐ | - Connections (are they suitably rated for output voltage and current, conventional styles, labelled etc.). |  |  |  |  |  |  |
| ☐ | - Heavy equipment fitted with suitable moving facilities e.g. handles, wheels, etc. |  |  |  |  |  |  |
| ☐ | - Documentation (schematics, service & operating information provided). |  |  |  |  |  |  |
| ☐ | - Leakage (RF, Light, heat, discharges, EMI, etc.) is within relevant ANU and Australian Standard’s. |  |  |  |  |  |  |
| 2. Equipment – Internal Wiring |  |  |  |  |  |  |  |
| ☐ | - Mains wiring segregated from isolated wiring (extra-low voltage, other inputs or outputs, etc.). |  |  |  |  |  |  |
| ☐ | - Wiring appropriately insulated and protected from abrasion/heat etc., secured in place. |  |  |  |  |  |  |
| ☐ | - Mains wiring using the correct insulation ratings and colours. |  |  |  |  |  |  |
| 3. Connections |  |  |  |  |  |  |  |
| ☐ | - Creepage & clearance distances between terminals, connections, any exposed bare wires. |  |  |  |  |  |  |
| ☐ | - Earth secured appropriately and labelled correctly. |  |  |  |  |  |  |
| ☐ | - Crimped mains connections made with the correct crimp-tool (no soldering before crimping). |  |  |  |  |  |  |
| ☐ | - Screwed mains connections made without soldering or tinning wires. |  |  |  |  |  |  |
| ☐ | - No loose, damaged or broken strands in a wire connection. |  |  |  |  |  |  |
| ☐ | - PCB track clearance and width adequate for voltage and current. |  |  |  |  |  |  |
| 4. Components |  |  |  |  |  |  |  |
| ☐ | - All components used are suitably rated for voltage, current, power, temperature etc. |  |  |  |  |  |  |
| ☐ | - All major components are labelled and match their circuit diagram numbers. |  |  |  |  |  |  |
| ☐ | - No components with obvious damage, discolouring, etc. |  |  |  |  |  |  |
| ☐ | - Exposed heat-sinks remain safe to touch in operation (<50ºC). |  |  |  |  |  |  |
| 5. Mechanical |  |  |  |  |  |  |  |
| ☐ | - Adequate ventilation. |  |  |  |  |  |  |
| ☐ | - Chassis, insulation, components etc. adequately secured with appropriate fasteners. |  |  |  |  |  |  |
| 6. Other |  |  |  |  |  |  |  |
| ☐ | - Other - Please provide details below. |  |  |  |  |  |  |
| AUTHORISED PERSON DETAILS |  |  |  |  |  |  |  |
| Family Name |  |  |  |  | Given name |  |  |
| Dept/Unit/Section |  |  |  |  |  |  |  |
| School/Div/Centre |  |  |  |  |  |  |  |
| University ID |  | U |  |  |  |  |  |
| Signature |  |  |  |  |  | Date |  |